AFC.DOC

AIR-FLOW-CALC

Copyright (c) 1994

by J. W. Slusser

Snyder Creek Software

For your balancing act

--------------------------------

Disclaimer

----------------

The author makes no claims or warranties regarding the usefulness

or functionality of this program. It is provided "AS IS". You, the

user, accept full responsibility and liability for any problems or

damages associated with its operation.

Shareware Plug

-----------------------

A lot of time and effort has gone into this program. If you find it

useful please register it. The registration fee for this program is

$15.00. Send cash, check or money order drawn on "US" funds to:

James W. Slusser

RR2 Box 128

West Union, Il. 62477

Make sure your address is included on the check or M.O.. Registration

means you will be eligible for one (1) free upgrade.

About AIR-FLOW-CALC:

The program was developed to aid engineers and technicians in

tracking the performance of fan systems.

A fan's performance is subject to certain physical laws which are

commonly referred to as fan laws.  Performance of a fan at varying speeds

can be predicted through the use of these three basic fan laws.

1. The volume of air delivered by a fan varies in direct proportion

to its speed.

2. Static pressure varies as the square of the fan speed.

3. Power required to run the fan varies as the cube fan speed.

These laws are the basis of this program and the formulas used are

indicated in the program.

An IMPORTANT NOTE about adjusting fan speeds:

Before making any adjustments to the fan always check the

manufacturers recommended safe fan speeds and also the motor manufacturers

safe operating amps.

For this program to be useful to you some involvement in measuring

air flow would be required.  Knowing how to use a monometer and a pitot tube

to measure velocity pressures in air streams would be helpful.

The air flow calculations are based on standard air density of .075

lbs. per cu. foot.  Future versions will allow the user to enter air

temperatures and barometric pressures and calulate actual air densities.

THE MAIN MENU

Selection #1:

Allows you to enter your field collected data, duct type and size,

number of traverse points, and velocity pressure (VP), in inches of water

column, for each point.  It then does the calculations for you to establish:

a. The square root of each VP measured.

b. Multiplies the square root of the VP by 4005 to

establish the velocity at each point (standard air

density).

c. Calculates the average of all velocities.

d. Calculates duct area in square feet.

e. Multiplies the area times the average velocity to

establish the cubic feet of air per minute (CFM)

produced in any given duct.

f. Allows you to save the final results to a file for

future reference.

Selection #2:

Allows you to use the information you have in hand to calculate fan

speeds needed to produce the required CFM's.  Once the data has been entered

and a required speed has been calculated you will be able to enter the next

stage of the program, selection #3.

Selection #3:

Allows you to size the fan pulley or motor sheave to produce the

desired CFM.  When entering this area from inside the program, from selection

#2 area, the required speed is presented for you.  When you enter this area

from the main menu you must enter the required speed.  At any rate you have

two choices you can calculate the fan pulley or the motor sheave size, your

choice.

Selection #4:

Allows you to read existing files.  It searches the current directory

and lists all the files that are available for reading.  It then prompts you

for a filename.  When you enter a valid file name it displays the file for

reading.

Selection #5:

Allows you to print existing files.  Again this is like the read file

selection, it lists all available files in the AFC directory.

It will print any text file you ask for, including this one.

Selection #6:

Does just what it says, Quits.

AIR-FLOW-CALC was written and compiled with Borland's 'Turbo C++ 3.0.'

Copyright (c) 1992 by Borland International.

AFC.Exe was then compressed using PKLITE Professional Version 1.00

Copyright (c) 1990 PKWARE, Inc.

Your comments and suggestions are welcome anytime!

James W. Slusser

RR2 Box 128

West Union, Il. 62477

Snyder Creek BBS

(217) 826-8975

1200 - 14,400 bps 8-N-1

or

jslusser@prairienet.org